## 2022
Party | BD | DQI breach category | MTUs with DQI breach | Cause | Mitigation | Corrective Action | Corrective action live since
CREOS | 2022-06-12 | IGM replacement | 1 to 24 | Due to the major reconstruction work at the Flebour substation and the resulting database changes in our SCADA system, errors occurred in the D2CF and DACF exports. The error was a too high voltage on provisional busbars entered in the database (D6FLEB24 + D6FLEB25), not D6FLEB22 as indicated by Coreso. After analyzing the database, it was found that the problem was caused by a disconnected transformer. This transformer was transforming the voltage from the 65kV level directly to the temporary busbars (220kV D6FLEB24 + D6FLEB25) resulting in a voltage of 265kV. | Correction of the database as described | The problem was solved by database changes and since 13.06 the files are being exported error free. | 2022-06-13
CREOS | 2022-06-13 | IGM replacement | 1 to 24 | Due to the major reconstruction work at the Flebour substation and the resulting database changes in our SCADA system, errors occurred in the D2CF and DACF exports. The error was a too high voltage on provisional busbars entered in the database (D6FLEB24 + D6FLEB25), not D6FLEB22 as indicated by Coreso. After analyzing the database, it was found that the problem was caused by a disconnected transformer. This transformer was transforming the voltage from the 65kV level directly to the temporary busbars (220kV D6FLEB24 + D6FLEB25) resulting in a voltage of 265kV. | Correction of the database as described | The problem was solved by database changes and since 13.06 the files are being exported error free. | 2022-06-13
CREOS | 2022-06-14 | IGM replacement | 1 to 24 | Due to the major reconstruction work at the Flebour substation and the resulting database changes in our SCADA system, errors occurred in the D2CF and DACF exports. The error was a too high voltage on provisional busbars entered in the database (D6FLEB24 + D6FLEB25), not D6FLEB22 as indicated by Coreso. After analyzing the database, it was found that the problem was caused by a disconnected transformer. This transformer was transforming the voltage from the 65kV level directly to the temporary busbars (220kV D6FLEB24 + D6FLEB25) resulting in a voltage of 265kV. | Correction of the database as described | The problem was solved by database changes and since 13.06 the files are being exported error free. | 2022-06-13
CREOS | 2022-06-22 | IGM replacement | 6 to 24 | Due to the high number of files to be generated more or less simultaneously (CGMES and UCTE) files in a reduced timeframe it happened that the system was overloaded and thus some files were skipped | Generating files (CGMES, UCTE format) only of the necessary grid . (220kV) | Change setting in SCADA (Supervisory Control and Data Acquisition) | 2022-06-30
TENNET NL | 12/06/20022 | IGM replacement | 10 to 16 | Several generators were accidently in an isolated isle mode in the IGM due to a wrong manual submission of a scheduled outage of these generators. Due to this action the respective generators were still included in the GSLK and the local tool was forced to use these generators for NP shift. Since these generators are in isle mode they cannot contribute to any NP shift, causing our local tool to crash. | N/A | Operators have been informed about the wrong entry of the scheduled outages, including an instruction on how to properly submit the scheduled outage of a generator in the local IGM creation tool. | 2022-08-18
TENNET NL | 2022-06-20 | IGM replacement | 1 to 24 | During the export of the IGM model for some generators the PV status was automatically changed to PQ. This was caused by a wrong configuration of these generators in the local IGM creation tool. | N/A | For all generators we checked the settings with regards to PV or PQ, and correspondingly corrected the incorrect PV of PQ status for multiple generators. | 2022-08-18
CREOS | 2022-07-02 | IGM replacement | 1 to 24 | Due to some Warnings/Errors in IGM in the CGMES format different tests have been performed with the parameter setting of the SCADA system .Here in this case , unfortunately the dedicated setting skipped the transformers in the UCTE files thus creating IGM with no transformer definition | Reset of default setting in the SCADA System (SCADA: Supervisory Control and Data Acquisition) | Better coordination of internal tests and settings of the SCADA | 2022-07-08
CREOS | 2022-07-24 | IGM replacement | 1 to 24 | Cyberattack 22/23/07/22 ; A wrong format of the IGMs of CREOS | The DPO team has taken all necessary measures to protect our data. Among other things, thus for instance files couldn't be sent to the "external world". | All necessary steps from Creos IT and other involved departments have been applied | end of august 22
CREOS | 2022-07-27 | IGM replacement | 1 to 24 | Cyberattack 22/23/07/22 ; missing files of BD 27/07/2022, Problems 25/7 & 26/6 | The DPO team has taken all necessary measures to protect our data. Among other things , thus for instance files couldn't be sent to the "external world". | All necessary steps from Creos IT and other involved departments have been applied | end of august 22
CREOS | 2022-07-28 | IGM replacement | 1 to 24 | Cyberattack 22/23/07/22 ; missing files of BD 28/07/2022; Problems 25/7 & 26/7 | The DPO team has taken all necessary measures to protect our data.Among other things, thus for instance files couldn't be sent to the "external world". | All necessary steps from Creos IT and other involved departments have been applied | end of august 22
RTE | 2022-07-05 | IGM replacement | 17.30 to 23.30 | The issue was not properly an IGM replacement, but a handling of x-node inconsistency by the Merging Entity. This is only a Core internal process issue and has no consequence on the results, thus decision has been taken to exclude this from the DQI reports in the future. Still, RTE is working on reducing this type of issue. | N/A | N/A | N/A
RTE | 2022-07-07 | IGM replacement | 0.30 to 23.30 | The issue was not properly an IGM replacement, but a handling of x-node inconsistency by the Merging Entity. This is only a Core internal process issue and has no consequence on the results, thus decision has been taken to exclude this from the DQI reports in the future. Still, RTE is working on reducing this type of issue. | N/A | N/A | N/A
SEPS | 2022-07-04 | IGM replacement | 1 to 24 | There was an issue with the voltage regulation in node QLEME that increased voltage above the predefined limits | Correction of the voltage regulation in node QLEME that was causing the troubles with convergence | Update of the IGM creation | 2022-07-09
SEPS | 2022-07-05 | IGM replacement | 1 to 24 | There was an issue with the voltage regulation in node QLEME that increased voltage above the predefined limits | Correction of the voltage regulation in node QLEME that was causing the troubles with convergence | Update of the IGM creation | 2022-07-09
SEPS | 2022-07-20 | IGM replacement | 1 to 24 | The IGM did not contain Pmin/Pmax limit for node that is included in the GLSK file and that led to the issue with merging | Data quality checks introduced in order to check whether all nodes from GLSK have Pmin/Pmax limits defined in the IGM | New data quality checks introduced | 2022-07-26
TENNET NL | 2022-07-17 | IGM replacement | N/A | X-node inconsistencies are wrongly translated to IGM replacement. So on this BD no real IGM replacement occurred, only X-node inconsistency cause a technical replacement at Coreso side. | none | manual correction in IGM creation | 2022-07-17
TENNET NL | 2022-07-20 | IGM replacement | only MTU 24 | Wrong IGM format for one MTU. Single occurence. | None |  | 2022-07-20
TSCNET | 2022-09-12 | NRAO results not applied | 1 to 14 and 19 to 24 | Ambiguity in the starting procedure of specific NRAO service application components on the vendor side, which lead to application component shutdowns. | Vendor implemented application component restart scripts. This measure was unsuccesful. | Restart scripts were shut down and removed on the 22.09.22. The correct application component starting procedure was redefined, documented, and shared with all support levels via workshops. Implemented a 24/7 application components monitoring and notiffication system to ensure all componentes are running. | 22.09.2022
TSCNET | 2022-09-17 | NRAO results not applied | 1 to 9 | Ambiguity in the starting procedure of specific NRAO service application components on the vendor side, which lead to application component shutdowns. | Vendor implemented application component restart scripts. This measure was unsuccesful. | Restart scripts were shut down and removed on the 22.09.22. The correct application component starting procedure was redefined, documented, and shared with all support levels via workshops. Implemented a 24/7 application components monitoring and notiffication system to ensure all componentes are running. | 22.09.2022
TSCNET | 2022-09-21 | NRAO results not applied | 1 to 24 | Ambiguity in the starting procedure of specific NRAO service application components on the vendor side, which lead to application component shutdowns. | Vendor implemented application component restart scripts. This measure was unsuccesful. | Restart scripts were shut down and removed on the 22.09.22. The correct application component starting procedure was redefined, documented, and shared with all support levels via workshops. Implemented a 24/7 application components monitoring and notiffication system to ensure all componentes are running. | 22.09.2022
TSCNET | 2022-09-22 | NRAO results not applied | 1 to 24 | Ambiguity in the starting procedure of specific NRAO service application components on the vendor side, which lead to application component shutdowns. | Vendor implemented application component restart scripts. This measure was unsuccesful. | Restart scripts were shut down and removed on the 22.09.22. The correct application component starting procedure was redefined, documented, and shared with all support levels via workshops. Implemented a 24/7 application components monitoring and notiffication system to ensure all componentes are running. | 22.09.2022
ELES | 2022-10-17 | IGM replacement | 23 and 24 | The ICGM merging failed due to issue during the PST Divaca and Pardiciano special procedure. This happened due to the fact that there was no active generation in Eles IGM. | CORESO to fix merging tool to avoid process fail is such cases | Merging tool fixed. | 1.12.2022
ELES | 2022-10-18 | IGM replacement | 1 to 24 | The ICGM merging failed due to issue during the PST Divaca and Pardiciano special procedure. This happened due to the fact that there was no active generation in Eles IGM. | CORESO to fix merging tool to avoid process fail is such cases | Merging tool fixed. | 1.12.2022
ELES | 2022-10-19 | IGM replacement | 1 to 24 | The ICGM merging failed due to issue during the PST Divaca and Pardiciano special procedure. This happened due to the fact that there was no active generation in Eles IGM. | CORESO to fix merging tool to avoid process fail is such cases | Merging tool fixed. | 1.12.2022
ELES | 2022-10-20 | IGM replacement | 7, 8 and 17 | The ICGM merging failed due to issue during the PST Divaca and Pardiciano special procedure. This happened due to the fact that there was no active generation in Eles IGM. | CORESO to fix merging tool to avoid process fail is such cases | Merging tool fixed. | 1.12.2022
ELES | 2022-10-21 | IGM replacement | 10 to 16 and 22 to 24 | The ICGM merging failed due to issue during the PST Divaca and Pardiciano special procedure. This happened due to the fact that there was no active generation in Eles IGM. | CORESO to fix merging tool to avoid process fail is such cases | Merging tool fixed. | 1.12.2022
ELES | 2022-10-22 | IGM replacement | 9 to 12 and 17 | The ICGM merging failed due to issue during the PST Divaca and Pardiciano special procedure. This happened due to the fact that there was no active generation in Eles IGM. | CORESO to fix merging tool to avoid process fail is such cases | Merging tool fixed. | 1.12.2022
CORESO | 2022-11-07 | Default flow-based parameters | 1 to 7 | DFPs triggered for MTUs 1 to 7 of BD 07/11/2022 following a failed FB computation due to high DC imbalance (5% imbalance threshold was reached). The root cause of this imbalance lies in the merging process: - A human error occurred during the update of a configuration of the CC DA IN process, leading to a misconfiguration of the CC DA CORE merging process (loss of X-nodes list required for the merging) -This caused a wrong computation of the final net positions in the CGM and divergences between the CGM and RefProg. | Configuration was corrected on the day after the event. | As a corrective action, a quality check has been introduced in our local communications tool, so that such a misconfiguration in the merging process will be detected by the operator immediately after the merging has been performed, and the merging process can be restarted. Additionally, a development of the merging tool is planned for 2023 that would make this error impossible by improving the handling of the X-node configuration. | 20.12.2022
TSCNET | 2022-12-15 | NRAO results not applied | 10 | Root cause is under investigation at the moment. Working hypothesis: AMPRION environment hardware specificites cause GROM subcomponent to fail on Production evnironment due to insufficient memory. | No mitigation actions were available. | Root cause is under investigation at the moment with all GROM support levels, TSCNET IT and Amprion staff. If working hypothesis is confirmed -> TSCNET will asses possible corrective actions, as extending memory on affected machines of Amprion Production environment and proceed on priority.
TSCNET | 2022-12-17 | NRAO results not applied | 8 | Root cause is under investigation at the moment. Working hypothesis: AMPRION environment hardware specificites cause GROM subcomponent to fail on Production evnironment due to insufficient memory. | No mitigation actions were available. | Root cause is under investigation at the moment with all GROM support levels, TSCNET IT and Amprion staff. If working hypothesis is confirmed -> TSCNET will asses possible corrective actions, as extending memory on affected machines of Amprion Production environment and proceed on priority.
TSCNET | 2022-12-18 | NRAO results not applied | 14,15,20 | Root cause is under investigation at the moment. Working hypothesis: AMPRION environment hardware specificites cause GROM subcomponent to fail on Production evnironment due to insufficient memory. | No mitigation actions were available. | Root cause is under investigation at the moment with all GROM support levels, TSCNET IT and Amprion staff. If working hypothesis is confirmed -> TSCNET will asses possible corrective actions, as extending memory on affected machines of Amprion Production environment and proceed on priority.
TSCNET | 2022-12-19 | NRAO results not applied | 2023-12-10 | Root cause is under investigation at the moment. Working hypothesis: AMPRION environment hardware specificites cause GROM subcomponent to fail on Production evnironment due to insufficient memory. | No mitigation actions were available. | Root cause is under investigation at the moment with all GROM support levels, TSCNET IT and Amprion staff. If working hypothesis is confirmed -> TSCNET will asses possible corrective actions, as extending memory on affected machines of Amprion Production environment and proceed on priority.
TSCNET | 2022-12-22 | NRAO results not applied | 1-17, 19-24 | Improper GROM subcomponent handling logic for a rare case where spanning is applied (for affected BD, CGM for one TS was missing in the inputs provided by CCCtool ) | No mitigation actions were available, TSCNET directly proceeded with corrective actions after failures occurred. | New version of GROM application subcomponent was developed, released and extensively tested in handling cases where spanning is applied. Deployment on Production environment expected in CW6 (6.2-10.2.)
TSCNET | 2022-12-25 | NRAO results not applied | 1-23 | Improper GROM subcomponent handling logic for a rare case where spanning is applied (for affected BD, CGM for one TS was missing in the inputs provided by CCCtool ) | No mitigation actions were available, TSCNET directly proceeded with corrective actions after failures occurred. | New version of GROM application subcomponent was developed, released and extensively tested in handling cases where spanning is applied. Deployment on Production environment expected in CW6 (6.2-10.2.)
TSCNET | 2022-12-27 | NRAO results not applied | 2017-11-01 | Root cause is under investigation at the moment. Working hypothesis: AMPRION environment hardware specificites cause GROM subcomponent to fail on Production evnironment due to insufficient memory. | No mitigation actions were available. | Root cause is under investigation at the moment with all GROM support levels, TSCNET IT and Amprion staff. If working hypothesis is confirmed -> TSCNET will asses possible corrective actions, as extending memory on affected machines of Amprion Production environment and proceed on priority.
CORESO | 15/12/2022 23/12/2022 24/12/2022 25/12/2022 26/12/2022 27/12/2022 28/12/2022 | Castor results not delivered | 15/12/2022 - 3,6,19,22,24 23/12/2022 - 8,16,23 24/12/2022 - 13,17,20 25/12/2022 - 1,3,10,12,14 26/12/2022 - 3,9,11 27/12/2022 - 1,9,14,17,20 28/12/2022 - 15,16,19,21,23 | Castor failed due to an IT infrastructure issue. | Coreso to fix infrastructure issue causing Castor to fail | Software patched | 20.01.2022
CORESO | 2022-12-22 | Spanning | 18 | Merging for timestamps 17:30 (MTU 18) failed du to BCI issue which lead to spanning. The issue was known and accepted as a risk before go-live. | Improvements to be made to merging server | Improvements to correct BCI issue included in develpment scope for April 2023
CORESO | 2022-12-25 | Default flow-based parameters | 24 | DFP triggered for MTU 24 of BD 25/12/2022 following a merging failure caused by a BCI issue. The issue was known and accepted as a risk before go-live. | Improvements to be made to merging server | Improvements to correct BCI issue included in develpment scope for April 2023

## 2023
Party | BD | DQI breach category | MTUs with DQI breach | Cause | Mitigation | Corrective Action | Corrective action live since
Creos | 2023-08-07 | IGM Replacement | 1 to 24 | Xchange server; transmission problem ; root cause not tangible | restart of Server | N/A | 2023-08-07
Creos | 2023-08-08 | IGM Replacement | 1 to 24 | Xchange server ; transmission mproblem root cause not tangible | restart of Server | N/A | 2023-08-07
TENNET NL | 2023-09-19 | IGM Replacement | 1 to 24 | Tool failure | Restart | N/A | 2023-09-19
TENNET NL | 2023-09-25 | IGM Replacement | 1 to 24 | Tool failure | Restart | N/A | 2023-09-25
MAVIR | 2023-09-19 | IGM Replacement | 1 to 24 | Tool failure | Restart | N/A | 2023-09-19
MAVIR | 2023-09-22 | IGM Replacement | 24 to 24 | Tool failure | Restart | N/A | 2023-09-22
MAVIR | 2023-09-22 | IGM Replacement | 1 to 24 | Tool failure | Restart | N/A | 2023-09-23
Coreso as CCCt operator | 2023-10-22 | DFP | 24 | Pre-Final FB Computation “Empty FB domain detected“. Root cause ECP connection issue The condition for application of is that spanning computation can be computed only in case one or two consecutive timestamps fail in normal computation and there are surrounding timestamps with success in normal computation. This condition cannot be satisfied for the first or last timestamp because there is at most one surrounding successful timestamp computation. Hence, the 24th timestamp defaulted to regular computation due to this limitation. | The issue was solved by maintenance support | N/A | 2023-10-23
Creos | 2023-12-08 | IGM Replacement | 1 to 24 | The setting of allowable difference between the market schedules and system calculation was exceeded , thus leading to a blockage of file (DACF,D2CF) generation | Re-Adjustement of parameter needed | The problem was solved by increasing this (Delta) parameter | 2023-12-15
Creos | 2023-12-09 | IGM Replacement | 1 to 24 | The setting of allowable difference between the market schedules and system calculation was exceeded , thus leading to a blockage of file (DACF,D2CF) generation | Re-Adjustement of parameter needed | The problem was solved by increasing this (Delta) parameter | 2023-12-15
Creos | 2023-12-12 | IGM Replacement | 1 to 24 | The setting of allowable difference between the market schedules and system calculation was exceeded , thus leading to a blockage of file (DACF,D2CF) generation | Re-Adjustement of parameter needed | The problem was solved by increasing this (Delta) parameter | 2023-12-15
Creos | 2023-12-13 | IGM Replacement | 1 to 24 | The setting of allowable difference between the market schedules and system calculation was exceeded , thus leading to a blockage of file (DACF,D2CF) generation | Re-Adjustement of parameter needed | The problem was solved by increasing this (Delta) parameter | 2023-12-15
Creos | 2023-12-14 | IGM Replacement | 1 to 24 | The setting of allowable difference between the market schedules and system calculation was exceeded , thus leading to a blockage of file (DACF,D2CF) generation | Re-Adjustement of parameter needed | The problem was solved by increasing this (Delta) parameter | 2023-12-15